## Sheet1
CATERPILLAR® POWER PRODUCTS
LOAD BANK TEST REPORT
(317) 545-2151
CUSTOMER: | MacAllister Power Systems | [6 empty] | SITE: |  | Indianapolis |  |  |  |  | Job# | CFS-WO-1031005
Pre-Start up Checks: | [12 empty] | Test Date: | 2019-02-08
| x | 1. Eng. Oil Level |  | x | 4. Safety ground connected | [7 empty] | Tested By: | Bill Peters
| x | 2. Coolant Level |  | x | 5. Circuit breaker open (off) | [7 empty] | Title: | GEN TECH
| x | 3. Generator and load bank connected for proper volts | [10 empty] | Tested At: | 100%
[12 empty] | Ambient Temp: |  | 18 degrees F
Engine Model: | [9 empty] | Serial Number: |  |  |  | KW: | 500
Generator Mfg/Model: | [9 empty] | Serial Number:
Control Panel Mfg: | [9 empty] | Serial Number:
Engine Safeties - Operational Test and/or Set Points:
Low Oil Pressure: |  | 30 |  | PSI |  |  | Overspeed: |  | 2120 |  |  |  | RPM: | 1800
Hi Water Temp: |  | 225 |  | F |  |  |  | Hours Before: | 809 |  |  |  | Hours After: | 810
Test Load/Duration: |  | 96:00 | [11 empty] | Min. Record Intervals
TIME | VOLTS |  |  |  |  | AMPS |  |  |  |  | FREQ HZ | LOAD KW | COOL TEMP F | Lube Oil | FUEL PRESS | % OF LOAD
| 1 |  | 2 | 3 |  | 1 |  | 2 |  | 3
13:00 | 478 |  | 478 | 478 |  | 0 |  | 0 |  | 0 | 60.4 | 0 | 110 | 72 |  | 0%
13:15 | 477 |  | 477 | 478 |  | 188 |  | 188 |  | 168 | 60.4 | 155.6444 | 175 | 68 |  | 31.13%
13:30 | 479 |  | 479 | 480 |  | 347 |  | 343 |  | 307 | 60.6 | 288.4819 | 175 | 65 |  | 57.7%
13:45 | 479 |  | 480 | 481 |  | 518 |  | 512 |  | 456 | 60.4 | 431.5417 | 178 | 60 |  | 86.31%
14:00 | 479 |  | 480 | 482 |  | 652 |  | 582 |  | 527 | 57.5 | 544.3052 | 180 | 58 |  | 108.9%
14:15 | 479 |  | 480 | 482 |  | 600 |  | 596 |  | 562 | 60 | 500.8944 | 180 | 60 |  | 100.2%
14:30 | 479 |  | 480 | 482 |  | 600 |  | 596 |  | 562 | 60 | 500.8944 | 180 | 60 |  | 100.2%
14:45 | 479 |  | 480 | 482 |  | 600 |  | 596 |  | 562 | 60 | 500.8944 | 180 | 60 |  | 100.2%
15:00 | 479 |  | 480 | 482 |  | 600 |  | 596 |  | 562 | 60 | 500.8944 | 180 | 60 |  | 100.2%
15:15 | 478 |  | 479 | 478 |  | 0 |  | 0 |  | 0 | 60.3 | 0 | 172 | 68 |  | 0%
15:30 | [11 empty] | 0 |  |  |  | 0%
15:45 | [11 empty] | 0 |  |  |  | 0%
16:00 | [11 empty] | 0 |  |  |  | 0%
16:15 | [11 empty] | 0 |  |  |  | 0%
16:30 | [11 empty] | 0 |  |  |  | 0%
16:45 | [11 empty] | 0 |  |  |  | 0%
17:00 | [11 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | 0%
[12 empty] | 0 |  |  |  | #DIV/0!
Customer Witness Acceptance: | [8 empty] | MacAllister Engine Power Approval:
By: | [8 empty] | By:
Title: | [8 empty] | Title:
SMM/MEP/072800 | [15 empty] | Page 1 of